## ref_power_unit_class
| This is the main Look-up table with defined values for plant categories. | [5 empty] | Efficiency of power generation |  |  | CHP thermal efficiency |  |  | CHP electric efficiency |  |  | CHP total efficiency |  |  | Availability factor |  |  | Minimum power for stable generation |  |  | Ramping up rate |  |  | Ramping down rate |  |  | Minimum up time |  |  | Minimum down time |  |  | Capital costs |  |  | Fixed O&M costs |  |  | Variable O&M costs |  |  | Start-up costs for hot start |  |  | Start-up costs for warm start |  |  | Start-up costs for cold start |  |  | Ramping costs |  |  | Start-up times for hot start |  |  | Start-up times for warm start |  |  | Start-up times for cold start
[7 empty] | % | % | % | % | % | % | % | % | % | % | % | % | % in time | % in time | % in time | % maximum capacity | % maximum capacity | % maximum capacity | % maximum capacity/ min. | % maximum capacity/min. | % maximum capacity/min. | % maximum capacity/min. | % maximum capacity/min. | % maximum capacity/min. | h | h | h | h | h | h | EUR/kW | EUR/kW | EUR/kW | EUR/kW/a | EUR/kW/a | EUR/kW/a | EUR/MWh | EUR/MWh | EUR/MWh | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | min. | min. | min. | h | h | h | h | h | h
| Energy carrier | Reference technology | Operative Features | Age bin | Size bin | Turbine Type | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max
| Hard coal / Lignite | Steam turbine (hard coal) | Sub-critical | <10 | L (>=400MW) |  | 38.5698 | 39.7207 | 40.8715 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 1.5 | 2.25 | 3 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | M (>=150MW and <400MW) |  | 35.7859 | 37.1743 | 38.5627 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 1.5 | 2.25 | 3 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | S (>=7.5MW and <150MW) |  | 27.2828 | 31.5249 | 35.7669 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 1.5 | 2.25 | 3 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | XS (<7.5MW) |  | 21.5638 | 24.4043 | 27.2447 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 1.5 | 2.25 | 3 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
|  |  |  | 10 - 30 | L (>=400MW) |  | 37.8244 | 38.953 | 40.0816 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | M (>=150MW and <400MW) |  | 35.0942 | 36.4558 | 37.8174 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | S (>=7.5MW and <150MW) |  | 26.7555 | 30.9156 | 35.0756 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | XS (<7.5MW) |  | 21.147 | 23.9326 | 26.7182 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
|  |  |  | >30 | L (>=400MW) |  | 36.6053 | 37.6976 | 38.7898 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | M (>=150MW and <400MW) |  | 33.9632 | 35.2809 | 36.5986 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | S (>=7.5MW and <150MW) |  | 25.8932 | 29.9192 | 33.9452 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
[5 empty] | XS (<7.5MW) |  | 20.4655 | 23.1613 | 25.8571 | - |  | - | - |  | - | - |  | - | 83.8 | 84.4 | 85 | 50 | 35 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 9.5 | 16 | 2 | 8.5 | 15 | 715 | 1107.5 | 1500 | 19.9 | 24.95 | 30 | 2 | 5.75 | 9.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.5 | 1.65 | 1.8 | 60 | 120 | 180 | 1.4 | 3.7 | 6 | 1.3 | 5.65 | 10
|  | Steam turbine (hard coal) | supercritical | <10 | L (>=400MW) |  | 41.7383 | 42.9837 | 44.2291 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | M (>=150MW and <400MW) |  | 38.7256 | 40.2281 | 41.7306 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | S (>=7.5MW and <150MW) |  | 29.5241 | 34.1146 | 38.7051 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | XS (<7.5MW) |  | 23.3352 | 26.409 | 29.4828 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
|  |  |  | 10 - 30 | L (>=400MW) |  | 38.4335 | 39.5803 | 40.7271 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | M (>=150MW and <400MW) |  | 35.6594 | 37.0429 | 38.4264 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | S (>=7.5MW and <150MW) |  | 27.1864 | 31.4134 | 35.6405 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | XS (<7.5MW) |  | 21.4876 | 24.318 | 27.1485 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
|  |  |  | >30 | L (>=400MW) |  | 36.6053 | 37.6976 | 38.7898 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 2 | 8.5 | 15 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | M (>=150MW and <400MW) |  | 33.9632 | 35.2809 | 36.5986 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 2 | 8.5 | 15 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | S (>=7.5MW and <150MW) |  | 25.8932 | 29.9192 | 33.9452 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 2 | 8.5 | 15 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | XS (<7.5MW) |  | 20.4655 | 23.1613 | 25.8571 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 2 | 8.5 | 15 | 715 | 1530.5 | 2346 | 14.7 | 28.85 | 43 | 2 | 4 | 6 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.3 | 1.55 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
|  | Steam turbine (hard coal) | ultra-supercritical | <10 | L (>=400MW) |  | 42.4439 | 43.7104 | 44.9768 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | M (>=150MW and <400MW) |  | 39.3803 | 40.9082 | 42.4361 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | S (>=7.5MW and <150MW) |  | 30.0232 | 34.6913 | 39.3594 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | XS (<7.5MW) |  | 23.7297 | 26.8555 | 29.9813 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
|  |  |  | 10 - 20 | L (>=400MW) |  | 41.9218 | 43.1726 | 44.4235 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | M (>=150MW and <400MW) |  | 38.8959 | 40.405 | 41.914 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | S (>=7.5MW and <150MW) |  | 29.6539 | 34.2646 | 38.8752 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
[5 empty] | XS (<7.5MW) |  | 23.4378 | 26.5251 | 29.6125 | - |  | - | - |  | - | - |  | - | 82 | 86.6 | 91.2 | 50 | 35 | 20 | 0.66 | 4.33 | 8 | 0.66 | 3.33 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 715 | 1530.5 | 2346 | 15.4 | 37.2 | 59 | 3 | 4.315 | 5.63 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 60 | 180 | 300 | 2 | 5 | 8 | 4 | 8 | 12
|  | Steam turbine (lignite) | Sub-critical | <10 | L (>=400MW) |  | 38.5698 | 39.7207 | 40.8715 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 1.5 | 2.25 | 3 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 35.7859 | 37.1743 | 38.5627 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 1.5 | 2.25 | 3 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 27.2828 | 31.5249 | 35.7669 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 1.5 | 2.25 | 3 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 21.5638 | 24.4043 | 27.2447 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 1.5 | 2.25 | 3 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
|  |  |  | 10 - 30 | L (>=400MW) |  | 37.8244 | 38.953 | 40.0816 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 35.0942 | 36.4558 | 37.8174 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 26.7555 | 30.9156 | 35.0756 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 21.147 | 23.9326 | 26.7182 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
|  |  |  | >30 | L (>=400MW) |  | 36.6053 | 37.6976 | 38.7898 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 33.9632 | 35.2809 | 36.5986 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 25.8932 | 29.9192 | 33.9452 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 20.4655 | 23.1613 | 25.8571 | - |  | - | - |  | - | - |  | - | 85 | 85.65 | 86.3 | 60 | 40 | 20 | 0.58 | 4.29 | 8 | 0.58 | 4.29 | 8 | 3 | 13.5 | 24 | 6 | 8 | 10 | 1400 | 1680.5 | 1961 | 31.1 | 34.05 | 37 | 2.6 | 6.55 | 10.5 | 8.4 | 39.45 | 70.5 | 46 | 81.5 | 117 | 67 | 88.5 | 110 | 1.8 | 1.8 | 1.8 | 120 | 240 | 360 | 4 | 5.5 | 7 | 5 | 8.9 | 12.8
|  | Steam turbine (lignite) | supercritical | <10 | L (>=400MW) |  | 40.0313 | 41.2258 | 42.4203 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 37.1419 | 38.5829 | 40.024 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 28.3167 | 32.7194 | 37.1222 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 22.3809 | 25.329 | 28.2771 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
|  |  |  | 10 - 30 | L (>=400MW) |  | 37.9785 | 39.1117 | 40.245 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 35.2372 | 36.6044 | 37.9715 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 26.8646 | 31.0416 | 35.2185 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 21.2332 | 24.0301 | 26.8271 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
|  |  |  | >30 | L (>=400MW) |  | 36.6053 | 37.6976 | 38.7898 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 6 | 8 | 10 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 33.9632 | 35.2809 | 36.5986 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 6 | 8 | 10 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 25.8932 | 29.9192 | 33.9452 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 6 | 8 | 10 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 20.4655 | 23.1613 | 25.8571 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 6 | 8 | 10 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
|  | Steam turbine (lignite) | ultra-supercritical | <10 | L (>=400MW) |  | 40.8658 | 42.0852 | 43.3046 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 37.9161 | 39.3872 | 40.8583 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 28.907 | 33.4015 | 37.896 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 22.8475 | 25.857 | 28.8666 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
|  |  |  | 10 - 20 | L (>=400MW) |  | 40.3631 | 41.5675 | 42.7719 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | M (>=150MW and <400MW) |  | 37.4497 | 38.9027 | 40.3557 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | S (>=7.5MW and <150MW) |  | 28.5514 | 32.9906 | 37.4299 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
[5 empty] | XS (<7.5MW) |  | 22.5664 | 25.5389 | 28.5115 | - |  | - | - |  | - | - |  | - | 85 | 90.15 | 95.3 | 60 | 40 | 20 | 0.58 | 3.29 | 6 | 0.58 | 3.29 | 6 | 3 | 6.5 | 10 | 1.5 | 2.25 | 3 | 998 | 1839 | 2680 | 26.6 | 31.8 | 37 | 2.6 | 6.55 | 10.5 | 3.56 | 22.03 | 40.5 | 5.7 | 26.85 | 48 | 6.2 | 42.1 | 78 | 1.8 | 1.8 | 1.8 | 78 | 159 | 240 | 2 | 3.5 | 5 | 5 | 8.9 | 12.8
|  | IGCC (Integrateg gasification combined cycle) |  |  | L (>=400MW) |  | 38.4 | 44.2 | 50 | - |  | - | - |  | - | - |  | - | 80 | 80 | 80 | 50 | 45 | 40 | 3 | 3.5 | 4 | 3 | 3.5 | 4 | no data |  | no data | no data |  | no data | 1400 | 2496.5 | 3593 | 40 | 51.5 | 63 | 3 | 6 | 9 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 180 | 300 | 420 | no data |  | no data | 80 | 90 | 100
[5 empty] | M (>=150MW and <400MW) |  | 38.4 | 44.2 | 50 | - |  | - | - |  | - | - |  | - | 80 | 80 | 80 | 50 | 45 | 40 | 3 | 3.5 | 4 | 3 | 3.5 | 4 | no data |  | no data | no data |  | no data | 1400 | 2496.5 | 3593 | 40 | 51.5 | 63 | 3 | 6 | 9 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 180 | 300 | 420 | no data |  | no data | 80 | 90 | 100
[5 empty] | S (>=7.5MW and <150MW) |  | 38.4 | 44.2 | 50 | - |  | - | - |  | - | - |  | - | 80 | 80 | 80 | 50 | 45 | 40 | 3 | 3.5 | 4 | 3 | 3.5 | 4 | no data |  | no data | no data |  | no data | 1400 | 2496.5 | 3593 | 40 | 51.5 | 63 | 3 | 6 | 9 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 180 | 300 | 420 | no data |  | no data | 80 | 90 | 100
[5 empty] | XS (<7.5MW) |  | 38.4 | 44.2 | 50 | - |  | - | - |  | - | - |  | - | 80 | 80 | 80 | 50 | 45 | 40 | 3 | 3.5 | 4 | 3 | 3.5 | 4 | no data |  | no data | no data |  | no data | 1400 | 2496.5 | 3593 | 40 | 51.5 | 63 | 3 | 6 | 9 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 180 | 300 | 420 | no data |  | no data | 80 | 90 | 100
|  | steam turbine (CHP) | Back-pressure |  | L (>=400MW) |  | - |  | - | 15 | 28.5 | 42 | 38 | 42 | 46 | 53 | 70.5 | 88 | 80 | 80 | 80 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | M (>=150MW and <400MW) |  | - |  | - | 15 | 28.5 | 42 | 38 | 42 | 46 | 53 | 70.5 | 88 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | S (>=7.5MW and <150MW) |  | - |  | - | 15 | 28.5 | 42 | 38 | 42 | 46 | 53 | 70.5 | 88 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | XS (<7.5MW) |  | - |  | - | 48 | 52.5 | 57 | 34 | 38 | 42 | 90 | 90.5 | 91 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | steam turbine (CHP) | Extraction |  | L (>=400MW) |  | - |  | - | 15 | 28.5 | 42 | 38 | 42 | 46 | 53 | 70.5 | 88 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | M (>=150MW and <400MW) |  | - |  | - | 15 | 28.5 | 42 | 38 | 42 | 46 | 53 | 70.5 | 88 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | S (>=7.5MW and <150MW) |  | - |  | - | 15 | 28.5 | 42 | 38 | 42 | 46 | 53 | 70.5 | 88 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | XS (<7.5MW) |  | - |  | - | 48 | 52.5 | 57 | 34 | 38 | 42 | 90 | 90.5 | 91 | 83.8 | 85.05 | 86.3 | 30 | 30 | 30 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | no data |  | no data | no data |  | no data | 2350 | 2500 | 2650 | 55.1 | 58.6 | 62.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Natural gas / Oil | Combined-cycle | Aero-derivative |  | L (>=350MW) |  | 55.38 | 58.63 | 61.88 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 3.125 | 6 | 0.5 | 3.25 | 6 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | M (>=100MW and <350MW) |  | 52.88 | 54.125 | 55.37 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 3.125 | 6 | 0.5 | 3.25 | 6 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | S (>=9MW and <100MW) |  | 51.97 | 52.42 | 52.87 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 3.125 | 6 | 0.5 | 3.25 | 6 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | XS (<9MW) |  | 51.89 | 51.925 | 51.96 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 3.125 | 6 | 0.5 | 3.25 | 6 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | no data |  | no data | no data |  | no data | no data |  | no data
|  | Combined-cycle | Heavy-duty | until 2000 | L (>=350MW) | E | 53.39 | 55.34 | 57.29 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 2.125 | 4 | 0.5 | 3.25 | 6 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 | 60 | 90 | 1 | 2.5 | 4 | 2 | 3.5 | 5
[5 empty] | M (>=100MW and <350MW) |  | 51.89 | 52.637 | 53.384 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 2.125 | 4 | 0.5 | 3.25 | 6 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 | 60 | 90 | 1 | 2.5 | 4 | 2 | 3.5 | 5
[5 empty] | S (>=9MW and <100MW) |  | 51.344 | 51.614 | 51.884 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 2.125 | 4 | 0.5 | 3.25 | 6 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 | 60 | 90 | 1 | 2.5 | 4 | 2 | 3.5 | 5
[5 empty] | XS (<9MW) |  | 51.296 | 51.317 | 51.338 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 2.125 | 4 | 0.5 | 3.25 | 6 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 | 60 | 90 | 1 | 2.5 | 4 | 2 | 3.5 | 5
|  |  |  | 2000-2005 | L (>=350MW) | Fa | 58.0514 | 59.3503 | 60.6492 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.625 | 3 | 0.5 | 1.75 | 3 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | M (>=100MW and <350MW) |  | 55.0966 | 56.5705 | 58.0445 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.625 | 3 | 0.5 | 1.75 | 3 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | S (>=9MW and <100MW) |  | 49.833 | 52.4533 | 55.0735 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.625 | 3 | 0.5 | 1.75 | 3 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | XS (<9MW) |  | 45.47 | 47.5294 | 49.5888 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 60 | 37.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.625 | 3 | 0.5 | 1.75 | 3 | 590 | 781 | 972 | 15.6 | 15.6 | 15.6 | 2.1 | 3.55 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
|  |  |  | 2006-2010 | L (>=350MW) | Fb | 60.505 | 60.7975 | 61.09 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | M (>=100MW and <350MW) |  | 60.28 | 60.392 | 60.5041 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | S (>=9MW and <100MW) |  | 60.1981 | 60.2386 | 60.2791 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | XS (<9MW) |  | 60.1909 | 60.194 | 60.1972 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
|  |  |  | After 2010 | L (>=350MW) | H | 61.26 | 61.91 | 62.56 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | M (>=100MW and <350MW) |  | 60.76 | 61.009 | 61.258 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | S (>=9MW and <100MW) |  | 60.578 | 60.668 | 60.758 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
[5 empty] | XS (<9MW) |  | 60.562 | 60.569 | 60.576 | - |  | - | - |  | - | - |  | - | 84 | 87.7 | 91.4 | 50 | 32.5 | 15 | 0.83 | 6.415 | 12 | 0.83 | 6.415 | 12 | 0.25 | 1.125 | 2 | 0.5 | 1.25 | 2 | 590 | 900 | 1210 | 17 | 18.5 | 20 | 1.3 | 3.15 | 5 | 1.5 | 13.85 | 26.2 | 1.5 | 21.4 | 41.3 | 3.5 | 39.725 | 75.95 | 0.25 | 0.375 | 0.5 | 30 |  | 60 | 1 |  | 1.5 | 2 | 2.5 | 3
|  | Gas turbine open cycle | Aero-derivative |  | L (>=350MW) |  | 48.3701 | 49.7425 | 51.1149 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 4 | 6 | 8 | 4 min. | 6 min. | 8 min. | 4 min. | 6 min. | 8 min.
[5 empty] | M (>=100MW and <350MW) |  | 42.5466 | 45.4513 | 48.3559 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 4 | 6 | 8 | 4 min. | 6 min. | 8 min. | 4 min. | 6 min. | 8 min.
[5 empty] | S (>=9MW and <100MW) |  | 33.249 | 37.8759 | 42.5028 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 4 | 6 | 8 | 4 min. | 6 min. | 8 min. | 4 min. | 6 min. | 8 min.
[5 empty] | XS (<9MW) |  | 26.55 | 29.7002 | 32.8504 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 4 | 6 | 8 | 4 min. | 6 min. | 8 min. | 4 min. | 6 min. | 8 min.
|  | Gas turbine open cycle | Heavy-duty | until 2000 | L (>=350MW) | E | 37.6603 | 38.1413 | 38.6224 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | M (>=100MW and <350MW) |  | 35.5158 | 36.5855 | 37.6553 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | S (>=9MW and <100MW) |  | 31.7307 | 33.6149 | 35.4991 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | XS (<9MW) |  | 28.63 | 30.0931 | 31.5563 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
|  |  |  | 2000-2005 | L (>=350MW) | Fa | 39.97 | 40.845 | 41.72 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | M (>=100MW and <350MW) |  | 38.22 | 39.0915 | 39.963 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | S (>=9MW and <100MW) |  | 37.583 | 37.898 | 38.213 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | XS (<9MW) |  | 37.527 | 37.5515 | 37.576 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 510 | 650 | 9 | 16.5 | 24 | 0.8 | 1 | 1.2 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
|  |  |  | 2006-2010 | L (>=350MW) | Fb | 39.97 | 40.845 | 41.72 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | M (>=100MW and <350MW) |  | 38.22 | 39.0915 | 39.963 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | S (>=9MW and <100MW) |  | 37.583 | 37.898 | 38.213 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | XS (<9MW) |  | 37.527 | 37.5515 | 37.576 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
|  |  |  | After 2010 | L (>=350MW) | H | 41.31 | 41.81 | 42.31 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | M (>=100MW and <350MW) |  | 40.31 | 40.808 | 41.306 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | S (>=9MW and <100MW) |  | 39.946 | 40.126 | 40.306 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
[5 empty] | XS (<9MW) |  | 39.914 | 39.928 | 39.942 | - |  | - | - |  | - | - |  | - | 60 | 75.05 | 90.1 | 50 | 35 | 20 | 0.83 | 15.415 | 30 | 0.83 | 15.415 | 30 | 0.1 | 0.55 | 1 | 0.25 | 0.625 | 1 | 370 | 550 | 730 | 9 | 16.5 | 24 | 0.8 | 2.4 | 4 | 0.02 | 12.01 | 24 | 0.02 | 47.26 | 94.5 | 0.06 | 38.53 | 77 | 0.66 | 0.73 | 0.8 | 0 | 15 | 30 | 0 | 0.25 | 0.5 | 0 | 0.5 | 1
|  | Steam turbine |  |  | L (>=350MW) |  | 33 | 40 | 47 | - |  | - | - |  | - | - |  | - | 60 | 74.5 | 89 | 40 | 40 | 40 | 0.58 | 3.79 | 7 | 0.58 | 3.79 | 7 | 0.25 | 3.125 | 6 | 1 | 3.5 | 6 | 920 | 920 | 920 | 16.6 | 16.6 | 16.6 | 1.5 | 1.8 | 2.1 | no data |  | no data | no data |  | no data | 40 | 40 | 40 | 1.17 | 1.17 | 1.17 | no data |  | no data | 1 | 1 | 1 | 2 | 2 | 2
[5 empty] | M (>=100MW and <350MW) |  | 33 | 40 | 47 | - |  | - | - |  | - | - |  | - | 60 | 74.5 | 89 | 40 | 40 | 40 | 0.58 | 3.79 | 7 | 0.58 | 3.79 | 7 | 0.25 | 3.125 | 6 | 1 | 3.5 | 6 | 920 | 920 | 920 | 16.6 | 16.6 | 16.6 | 1.5 | 1.8 | 2.1 | no data |  | no data | no data |  | no data | 40 | 40 | 40 | 1.17 | 1.17 | 1.17 | no data |  | no data | 1 | 1 | 1 | 2 | 2 | 2
[5 empty] | S (>=9MW and <100MW) |  | 33 | 40 | 47 | - |  | - | - |  | - | - |  | - | 60 | 74.5 | 89 | 40 | 40 | 40 | 0.58 | 3.79 | 7 | 0.58 | 3.79 | 7 | 0.25 | 3.125 | 6 | 1 | 3.5 | 6 | 920 | 920 | 920 | 16.6 | 16.6 | 16.6 | 1.5 | 1.8 | 2.1 | no data |  | no data | no data |  | no data | 40 | 40 | 40 | 1.17 | 1.17 | 1.17 | no data |  | no data | 1 | 1 | 1 | 2 | 2 | 2
[5 empty] | XS (<9MW) |  | 33 | 40 | 47 | - |  | - | - |  | - | - |  | - | 60 | 74.5 | 89 | 40 | 40 | 40 | 0.58 | 3.79 | 7 | 0.58 | 3.79 | 7 | 0.25 | 3.125 | 6 | 1 | 3.5 | 6 | 920 | 920 | 920 | 16.6 | 16.6 | 16.6 | 1.5 | 1.8 | 2.1 | no data |  | no data | no data |  | no data | 40 | 40 | 40 | 1.17 | 1.17 | 1.17 | no data |  | no data | 1 | 1 | 1 | 2 | 2 | 2
|  | Internal combustion |  |  | L (>=10MW) |  | 49.2927 | 50.4566 | 51.6205 | - |  | - | - |  | - | - |  | - | 84 | 87.05 | 90.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  |  | no data |  | no data | no data |  | no data | 1 | 1 | 1
[5 empty] | M (>=5MW and <10MW) |  | 45.5539 | 47.1296 | 48.7052 | - |  | - | - |  | - | - |  | - | 84 | 87.05 | 90.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1 | 1 | 1
[5 empty] | S (>=2MW and <5MW) |  | 41.0431 | 42.7274 | 44.4117 | - |  | - | - |  | - | - |  | - | 84 | 87.05 | 90.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1 | 1 | 1
[5 empty] | XS (<2MW) |  | 33.0734 | 36.9388 | 40.8042 | - |  | - | - |  | - | - |  | - | 84 | 87.05 | 90.1 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1 | 1 | 1
|  | CCGT (CHP) |  |  |  |  | - |  | - | 38 | 45.5 | 53 | 35 | 42.5 | 50 | 73 | 82.5 | 92 | 60 | 72.25 | 84.5 | 40 | 40 | 40 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 700 | 850 | 1000 | no data |  | no data | 0.04 | 0.04 | 0.04 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Gas turbine (CHP) |  |  |  |  | - |  | - | no data |  | no data | 50 | 52.5 | 55 | 65 | 75 | 85 | 93 | 94.5 | 96 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 250 | 250 | 250 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 0.166 | 0.583 | 1
|  | Internal combustion (CHP) |  |  |  |  | - |  | - | 47.1 | 49.6 | 52.1 | 38 | 39.5 | 41 | 88.2 | 89.2 | 90.2 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1292 | 2096 | 2900 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 10 sec |  | 10 sec
|  | steam turbine (CHP) | Back-pressure |  |  |  | - |  | - | 60 | 60 | 60 | 5 | 15 | 25 | 75 | 83.5 | 92 | 72 | 85.5 | 99 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | steam turbine (CHP) | Extraction |  |  |  | - |  | - | 60 | 60 | 60 | 5 | 15 | 25 | 60 | 72.5 | 85 | 72 | 85.5 | 99 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Uranium | Nuclear | PWR (Pressurized water reactor) |  | L (>=750MW) |  | 33 | 35.5 | 38 | - |  | - | - |  | - | - |  | - | 71 | 35.5 | 95.5 | 50 | 35 | 20 | 0.25 | 5.125 | 10 | 0.25 | 5.125 | 10 | 6 | 87 | 168 | 4 | 26 | 48 | 3000 | 5085.5 | 7171 | 5 | 57.5 | 110 | 0 | 2.5 | 5 | no data |  | no data | no data |  | no data | 16.7 | 78.35 | 140 | no data |  | no data | 20 | 130 | 240 | 2 | 6 | 10 | 24 | 37 | 50
[5 empty] | M (<750MW) |  | 33 | 35.5 | 38 | - |  | - | - |  | - | - |  | - | 71 | 35.5 | 95.5 | 50 | 35 | 20 | 0.25 | 5.125 | 10 | 0.25 | 5.125 | 10 | 6 | 87 | 168 | 4 | 26 | 48 | 3000 | 5085.5 | 7171 | 5 | 57.5 | 110 | 0 | 2.5 | 5 | no data |  | no data | no data |  | no data | 16.7 | 78.35 | 140 | no data |  | no data | 20 | 130 | 240 | 2 | 6 | 10 | 24 | 37 | 50
|  |  | BWR (Boiling water reactor) |  | L (>=750MW) |  | 33 | 33 | 33 | - |  | - | - |  | - | - |  | - | 71 | 35.5 | 95.5 | 60 | 40 | 20 | 0.25 | 5.125 | 10 | 0.25 | 5.125 | 10 | 6 | 87 | 168 | 4 | 26 | 48 | 3000 | 5085.5 | 7171 | 5 | 57.5 | 110 | 0 | 2.5 | 5 | no data |  | no data | no data |  | no data | 16.7 | 78.35 | 140 | no data |  | no data | 20 | 130 | 240 | 2 | 6 | 10 | 24 | 37 | 50
[5 empty] | M (<750MW) |  | 33 | 33 | 33 | - |  | - | - |  | - | - |  | - | 71 | 35.5 | 95.5 | 60 | 40 | 20 | 0.25 | 5.125 | 10 | 0.25 | 5.125 | 10 | 6 | 87 | 168 | 4 | 26 | 48 | 3000 | 5085.5 | 7171 | 5 | 57.5 | 110 | 0 | 2.5 | 5 | no data |  | no data | no data |  | no data | 16.7 | 78.35 | 140 | no data |  | no data | 20 | 130 | 240 | 2 | 6 | 10 | 24 | 37 | 50
| Biomass | Steam turbine |  |  |  |  | 30 | 35 | 40 | - |  | - | - |  | - | - |  | - | 85 | 85 | 85 | 30 | 30 | 30 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 883 | 2765.5 | 4648 | 116 | 120.5 | 125 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | steam turbine (CHP) | Back-pressure |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | no data |  | no data | 30 | 30 | 30 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 252 | 259.5 | 267 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | steam turbine (CHP) | Extraction |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | no data |  | no data | 30 | 30 | 30 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 252 | 259.5 | 267 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Organic Rankine-cycle (CHP) |  |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | no data |  | no data | 30 | 30 | 30 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Biogas | Internal combustion |  |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | 85 | 85 | 85 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 2015 | 2207.5 | 2400 | no data |  | no data | 31 | 31 | 31 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Internal combustion (CHP) |  |  |  |  | - |  | - | 26.86 | 26.86 | 26.86 | 28.45 | 28.45 | 28.45 | 87.05 | 87.05 | 87.05 | 85 | 85 | 85 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 2600 | 5487 | 8374 | 125 | 173.5 | 222 |  |  |  | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Water | Conventional hydroelectric turbine | Run-of-river |  | L (>=30MW) |  | 95 | 95 | 95 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1800 | 3391 | 4982 | 38 | 39.5 | 41 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | M (>=10MW and <30MW) |  | 95 | 95 | 95 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1800 | 3391 | 4982 | 41 | 41 | 41 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | S (>=1MW and <10MW) |  | 90 | 90 | 90 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1800 | 3391 | 4982 | 36 | 48 | 60 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | XS (<1MW) |  | 90 | 90 | 90 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1800 | 3391 | 4982 | 41 | 133 | 225 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  | Reservoirs |  | L (>=75MW) |  | 95 | 95 | 95 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1673 | 8825 | 15977 | 38 | 39.5 | 41 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | M (>=10MW and <75MW) |  | 95 | 95 | 95 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1673 | 8825 | 15977 | 41 | 41 | 41 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | S (>=1MW and <10MW) |  | 90 | 90 | 90 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1800 | 6689.5 | 11579 | 36 | 48 | 60 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | XS (<1MW) |  | 90 | 90 | 90 | - |  | - | - |  | - | - |  | - | 98 | 98 | 98 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 1800 | 6689.5 | 11579 | 41 | 133 | 225 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Pumped-storage |  |  | L (>=75MW) |  | 50 | 67.5 | 85 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 850 | 2482.9 | 4115.8 | 18 | 18 | 18 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | M (>=10MW and <75MW) |  | 50 | 67.5 | 85 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 850 | 2482.9 | 4115.8 | 18 | 18 | 18 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | S (>=1MW and <10MW) |  | 50 | 67.5 | 85 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 850 | 2482.9 | 4115.8 | 18 | 18 | 18 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
[5 empty] | XS (<1MW) |  | 50 | 67.5 | 85 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 850 | 2482.9 | 4115.8 | 18 | 18 | 18 | 0 | 0 | 0 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Tidal |  |  |  |  | 90 | 90 | 90 | - |  | - | - |  | - | - |  | - | no data |  | no data | 25 | 25 | 25 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 2250 | 3000 | 3750 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Wave |  |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | 90 | 90 | 90 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | 2694 | 4820.5 | 6947 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Solar | Photovoltaic | RESIDENTIAL ROOFTOP |  | XS (<0.01MW) |  | 16 | 19 | 22 | - | 0 | - | - | 0 | - | - | 0 | - | 8 | 15 | 22 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1600 | 2000 | 20 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Photovoltaic ) | COMMERCIAL ROOFTOP |  | S (>=0.01MW and <0.5MW) |  | 17 | 20 | 23 | - | 0 | - | - | 0 | - | - | 0 | - | 10 | 18 | 26 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1150 | 1400 | 15 | 22.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Photovoltaic ( | UTILITY SCALE |  | M (>=1MW and <100MW) |  | 18 | 21 | 24 | - | 0 | - | - | 0 | - | - | 0 | - | 12 | 22 | 32 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 20 | 10 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 |  | Photovoltaic () | LARGE SCALE |  | L (>=100MW) |  | 19 | 22 | 25 | - | 0 | - | - | 0 | - | - | 0 | - | 15 | 27.5 | 40 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 700 | 900 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | OFFSHORE | Standard depth (30-50m) Near shore (<50km) |  | L (>=20MW) |  | 49 | 52 | 55 | - | 0 | - | - | 0 | - | - | 0 | - | 40 | 47.5 | 55 | 0 | 0 | 0 | 20 | 35 | 50 | 20 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 2500 | 3000 | 60 | 85 | 110 | 3 | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=15MW and <20MW) |  | 47 | 50 | 53 | - | 0 | - | - | 0 | - | - | 0 | - | 38 | 45 | 52 | 0 | 0 | 0 | 20 | 35 | 50 | 20 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2200 | 2850 | 3500 | 70 | 95 | 120 | 4 | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=8MW and <15MW) |  | 45 | 48 | 51 | - | 0 | - | - | 0 | - | - | 0 | - | 35 | 42.5 | 50 | 0 | 0 | 0 | 20 | 35 | 50 | 20 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 3250 | 4000 | 80 | 110 | 140 | 5 | 8.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Deep water (>50m) Far offshore (>50km) |  | L (>=20MW) |  | 49 | 52 | 55 | - | 0 | - | - | 0 | - | - | 0 | - | 40 | 47.5 | 55 | 0 | 0 | 0 | 20 | 35 | 50 | 20 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 3500 | 4500 | 72 | 113 | 154 | 3.6 | 8.1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=15MW and <20MW) |  | 47 | 50 | 53 | - | 0 | - | - | 0 | - | - | 0 | - | 38 | 45 | 52 | 0 | 0 | 0 | 20 | 35 | 50 | 20 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2750 | 4000 | 5250 | 84 | 126 | 168 | 4.8 | 9.4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=8MW and <15MW) |  | 45 | 48 | 51 | - | 0 | - | - | 0 | - | - | 0 | - | 35 | 42.5 | 50 | 0 | 0 | 0 | 20 | 35 | 50 | 20 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 3125 | 4562.5 | 6000 | 96 | 146 | 196 | 6 | 11.4 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ONSHORE | Standard terrain Impact |  | L (>=8MW) | IEC Class III/IV (Low wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 26 | 37 | 48 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 1050 | 1300 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 22 | 31 | 40 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1150 | 1400 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 20 | 27.5 | 35 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1250 | 1500 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 18 | 25 | 32 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 1350 | 1600 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ONSHORE | Standard terrain Impact |  | L (>=8MW) | IEC Class II (Medium wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 31.98 | 45.51 | 59.04 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 1050 | 1300 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 27.06 | 38.13 | 49.2 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1150 | 1400 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 24.6 | 33.825 | 43.05 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1250 | 1500 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 22.14 | 30.75 | 39.36 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 1350 | 1600 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ONSHORE | Standard terrain Impact |  | L (>=8MW) | IEC Class I (High wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 43.16 | 61.42 | 79.68 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 1050 | 1300 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 36.52 | 51.46 | 66.4 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1150 | 1400 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 33.2 | 45.65 | 58.1 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1250 | 1500 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 29.88 | 41.5 | 53.12 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 1350 | 1600 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Simple terrain Impact (flat) |  | L (>=8MW) | IEC Class III/IV (Low wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 26 | 37 | 48 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 945 | 1170 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 22 | 31 | 40 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 1035 | 1260 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 20 | 27.5 | 35 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1125 | 1350 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 18 | 25 | 32 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 1215 | 1440 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Standard terrain Impact |  | L (>=8MW) | IEC Class II (Medium wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 31.98 | 45.51 | 59.04 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 945 | 1170 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 27.06 | 38.13 | 49.2 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 1035 | 1260 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 24.6 | 33.825 | 43.05 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1125 | 1350 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 22.14 | 30.75 | 39.36 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 1215 | 1440 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Standard terrain Impact |  | L (>=8MW) | IEC Class I (High wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 43.16 | 61.42 | 79.68 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 945 | 1170 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 36.52 | 51.46 | 66.4 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 1035 | 1260 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 33.2 | 45.65 | 58.1 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1125 | 1350 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 29.88 | 41.5 | 53.12 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 1215 | 1440 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Complex terrain Impact (mountainous) |  | L (>=8MW) | IEC Class III/IV (Low wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 26 | 37 | 48 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 1272.5 | 1625 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 22 | 31 | 40 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 1392.5 | 1750 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 20 | 27.5 | 35 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 1512.5 | 1875 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 18 | 25 | 32 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1265 | 1632.5 | 2000 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Standard terrain Impact |  | L (>=8MW) | IEC Class II (Medium wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 31.98 | 45.51 | 59.04 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 1272.5 | 1625 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 27.06 | 38.13 | 49.2 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 1392.5 | 1750 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 24.6 | 33.825 | 43.05 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 1512.5 | 1875 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 22.14 | 30.75 | 39.36 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1265 | 1632.5 | 2000 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Standard terrain Impact |  | L (>=8MW) | IEC Class I (High wind) | 35 | 42.5 | 50 | - | 0 | - | - | 0 | - | - | 0 | - | 43.16 | 61.42 | 79.68 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 1272.5 | 1625 | 18 | 29 | 40 | 5 | 9.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | M (>=5MW and <8MW) |  | 30 | 36 | 42 | - | 0 | - | - | 0 | - | - | 0 | - | 36.52 | 51.46 | 66.4 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 1392.5 | 1750 | 20 | 31 | 42 | 6 | 10.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | S (>=3MW and <5MW) |  | 28 | 33 | 38 | - | 0 | - | - | 0 | - | - | 0 | - | 33.2 | 45.65 | 58.1 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 1512.5 | 1875 | 22 | 33.5 | 45 | 7 | 11.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | XS (<3MW) |  | 25 | 30 | 35 | - | 0 | - | - | 0 | - | - | 0 | - | 29.88 | 41.5 | 53.12 | 0 | 0 | 0 | 15 | 27.5 | 40 | 15 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1265 | 1632.5 | 2000 | 25 | 37.5 | 50 | 8 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * (CHP) | cogeneration technologies
Note on AO3: all EUR/kWa; Nuclear (€/MWh)
Note on AP3: all EUR/kWa; Nuclear (€/MWh)
Note on AQ3: all EUR/kWa; Nuclear (€/MWh)

## References
| This is the list of references which were used to populate the main Look-up table |  |  |  |  | Efficiency of power generation |  |  | CHP thermal efficiency |  |  | CHP electric efficiency |  |  | CHP total efficiency |  |  | Availability factor |  |  | Minimum power for stable generation |  |  | Ramping up rate |  |  | Ramping down rate |  |  | Minimum up time |  |  | Minimum down time |  |  | Capital costs |  |  | Fixed O&M costs |  |  | Variable O&M costs |  |  | Start-up costs for hot start |  |  | Start-up costs for warm start |  |  | Start-up costs for cold start |  |  | Ramping costs |  |  | Start-up times for hot start |  |  | Start-up times for warm start |  |  | Start-up times for cold start
[6 empty] | % | % | % | % | % | % | % | % | % | % | % | % | % in time | % in time | % in time | % maximum capacity | % maximum capacity | % maximum capacity | % maximum capacity/ min. | % maximum capacity/min. | % maximum capacity/min. | % maximum capacity/min. | % maximum capacity/min. | % maximum capacity/min. | h | h | h | h | h | h | EUR/kW | EUR/kW | EUR/kW | EUR/kW/a | EUR/kW/a | EUR/kW/a | EUR/MWh | EUR/MWh | EUR/MWh | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | EUR/DMW | min. | min. | min. | h | h | h | h | h | h
| Energy carrier | Reference technology | Age bin | Size bin | Turbine type | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max | Min | Best | Max
| Hard coal / Lignite | Steam turbine - sub-critical | <10 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  | 10 - 30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  | >30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | DIW 2014 | DIW 2013 |  | Hentschel 2016 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, old) |  | DIW 2013 (Ehlers 2011) - coal fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | Bertsch 2016 | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016 | Parsons Brinckerhoff - DECC 2014 |  | Hentschel 2016
|  | Steam turbine - supercritical | <10 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2008
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2009
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2010
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2011
|  |  | 10 - 30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2012
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2013
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2014
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2015
|  |  | >30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2016
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2017
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2018
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - coal fired steam power plant, old |  | DIW 2013 (Schuewer et al. 2010) - coal fired steam power plant, old | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | DIW 2013 (IEA 2011b) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2019
|  | Steam turbine - ultra-supercritical | <10 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2020
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2021
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2022
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2023
|  |  | 10 - 20 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2024
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2025
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2026
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | dena 2008 | DIW 2013 |  | Hentschel 2016 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | IEA 2014 (coal fired steam power plant, new) |  | van der Bergh and Delarue 2015 (coal fired steam power plant, new) | Hentschel 2016, coal fired steam power plant |  | IEA 2014 - coal fired steam power plant, new | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (wagner 2004) |  | IEA 2016 | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (MIT 2007) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | diw 2012, Grimm 2007 |  | DIW 2013, Wacek 2010 | DIW 2013, Hundt el al. 2009 |  | DIW 2013,Meibom el al. 2000 | Ecofys 2014 |  | DIW 2013, Meibom et al. 2027
|  | Steam turbine - sub-critical (lignite) | <10 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  | 10 - 30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  | >30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | Bertsch 2016 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (IEA 2011a) |  | DIW 2013 (Klobasa et al.. 2009) | DIW 2013 (Klobasa et al. 2009) - lignite fired steam power plant, old |  | DIW 2013 (Ehlers 2011) - lignite fired steam power plant, old | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | Hentschel 2016 |  | DIW 2013 (RWI 1997) | DIW 2013 (Wagner 2004, Lignite Old) |  | DIW 2013 (EWI et al.. 2010, Lignite Old) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Grimm 2007) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Kumar et al. 2012 modern) |  | DIW 2013 (Kumar et al. 2012 median) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Hentschel 2016 |  | DIW 2013,VDE 2012 | Hentschel 2016 |  | Hentschel 2016 | Lund et al. 2015 |  | DIW 2013, Traber & Kemfert 2011
|  | Steam turbine - supercritical (lignite) | <10 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  | 10 - 30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  | >30 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | DIW 2013 (Hundt et al. 2009) - lignite fired steam power plant, old |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  | Steam turbine - ultra-supercritical (lignite) | <10 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  | 10 - 20 | L (>=400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=150MW and <400MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=7.5MW and <150MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<7.5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | DIW 2013 |  | Ecofys 2014 | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | DIW 2013 (IEA 2011a) |  | DIW 2013 (VDE 2012) | IEA 2014 lignite fired steam power plant, new) |  | van der Bergh and Delarue 2015 lignite fired steam power plant, new) | Hentschel 2016, lignite fired steam power plant |  | van der Bergh and Delarue 2015 (lignite fired steam power plant) | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2010) | DIW 2013 (Wagner 2004, Lignite New (BoA)) |  | DIW 2013 (EWI et al.. 2010, Lignite New (BoA)) | DIW 2013 (Traber & Kemfert 2010) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (dena 2005) |  | DIW 2013 (Kumar et al. 2012 modern) | Van der Bergh & Delarue 2015 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | DIW 2013,VDE 2012 | Hundt el al. 2009 |  | Siemens AG 2010 | Siemens AG 2010 |  | DIW 2013, Traber & Kemfert 2011
|  | IGCC (Integrateg gasification combined cycle) |  | L (>=400MW) |  | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2011b) | - |  | - | - |  | - | - |  | - | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | no data |  | no data | no data |  | no data | DIW (ECF 2010) |  | DIW (IEA 2010) | Brouwer 2010 |  | DIW 2013 (IEA 2011b) | Brouwer 2015 |  | DIW 2013 (IEA 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015
|  |  |  | M (>=150MW and <400MW) |  | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2011b) | - |  | - | - |  | - | - |  | - | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | no data |  | no data | no data |  | no data | DIW (ECF 2010) |  | DIW (IEA 2010) | Brouwer 2010 |  | DIW 2013 (IEA 2011b) | Brouwer 2015 |  | DIW 2013 (IEA 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015
|  |  |  | S (>=7.5MW and <150MW) |  | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2011b) | - |  | - | - |  | - | - |  | - | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | no data |  | no data | no data |  | no data | DIW (ECF 2010) |  | DIW (IEA 2010) | Brouwer 2010 |  | DIW 2013 (IEA 2011b) | Brouwer 2015 |  | DIW 2013 (IEA 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015
|  |  |  | XS (<7.5MW) |  | DIW 2013 (MIT 2007) |  | DIW 2013 (IEA 2011b) | - |  | - | - |  | - | - |  | - | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Tidball et al. 2010 Cost and Performance Assumptions for Modeling Electricity Generation Technologies | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | no data |  | no data | no data |  | no data | DIW (ECF 2010) |  | DIW (IEA 2010) | Brouwer 2010 |  | DIW 2013 (IEA 2011b) | Brouwer 2015 |  | DIW 2013 (IEA 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015 | Brouwer 2015 |  | Brouwer 2015
|  | Backpressure steam turbine (CHP) |  | L (>=400MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | M (>=150MW and <400MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | S (>=7.5MW and <150MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | XS (<7.5MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Extraction steam turbine (CHP) |  | L (>=400MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | M (>=150MW and <400MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | S (>=7.5MW and <150MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | XS (<7.5MW) |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | (coal) Bertsch 2016 |  | (lignite) Bertsch 2016 | Bertsch 2016 (lignite CHP, hard coal CHP) |  | Bertsch 2016 (lignite CHP, hard coal CHP) | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | DIW 2013 (ECF 2010); many techologies |  | DIW 2013 (ECF 2010); many techologies | no data |  | no data | no data |  | no data | Bertsch 2016 (lignite CHP) |  | Bertsch 2016 (hard coal CHP) | Bertsch 2016 (hard coal CHP) |  | Bertsch 2016 (lignite CHP) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Natural gas / Oil | Combined-cycle (aeroderivative) |  | L (>=350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT (heavy - duty) |  | DIW 2013 (Traber & Kemfert 2011); like CCGT (heavy - duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT (heavy - duty) |  | DIW 2013 (Traber & Kemfert 2011); like CCGT (heavy - duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT (heavy - duty) |  | DIW 2013 (Traber & Kemfert 2011); like CCGT (heavy - duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT (heavy - duty) |  | DIW 2013 (Traber & Kemfert 2011); like CCGT (heavy - duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015
|  | Combined-cycle (heavy-duty) | until 2000 | L (>=350MW) | E | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Hentschel 2016 | Siemens AG 2010 |  | DIW 2013, Meibom el al. 2000 | Hentschel 2016 |  | DIW 2013, Meibom et al. 2008
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Hentschel 2016 | Siemens AG 2010 |  | DIW 2013, Meibom el al. 2001 | Hentschel 2016 |  | DIW 2013, Meibom et al. 2008
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Hentschel 2016 | Siemens AG 2010 |  | DIW 2013, Meibom el al. 2002 | Hentschel 2016 |  | DIW 2013, Meibom et al. 2008
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | van der Bergh and Delarue 2015 (CCGT) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Hentschel 2016 | Siemens AG 2010 |  | DIW 2013, Meibom el al. 2003 | Hentschel 2016 |  | DIW 2013, Meibom et al. 2008
|  |  | 2000-2005 | L (>=350MW) | Fa | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | IAE 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGT old) | Hentschel 2016 (CCGT) |  | DIW 2013 (RWI 1997) | DIW 2013 (Capros 2011, Combined Cycle Old) |  | DIW 2013 (Capros 2011, Combined Cycle Old) | DIW 2013 (Capros 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  | 2006-2010 | L (>=350MW) | Fb | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  | After 2010 | L (>=350MW) | H | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | EWI et al. 2010; CCGT |  | dena 2008; CCGT | Ecofys 2014 |  | Ecofys 2014 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 (CCGT) |  | ECOFYS 2014 (CCGT new) | Hentschel 2016 (CCGT) |  | IEA 2014 (CCGTnew | Hentschel 2016 (CCGT) |  | DIW 2013 (IEA 2010, CCGT (new)) | DIW 2013 (IEA 2011b, Combined Cycle New) |  | DIW 2013 (Capros 2011, Combined Cycle New) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Traber & Kemfert 2011) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010 | Siemens AG 2010 |  | Siemens AG 2010
|  | Gas turbine open cycle (aeroderivative) |  | L (>=350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | DIW 2013 | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 modern); like CCGT(heavy - duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | DIW 2013 | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 modern); like CCGT(heavy - duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | DIW 2013 | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 modern); like CCGT(heavy - duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | DIW 2013 | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 modern); like CCGT(heavy - duty) | DIW 2013 (Meibom et al. 2008); like CCGT(heavy - duty) |  | DIW 2013 (Kumar et al. 2012 median); like CCGT (heavy duty) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014 | Parsons Brinckerhoff - DECC 2014 |  | Parsons Brinckerhoff - DECC 2014
|  | Gas turbine open cycle (heavy-duty) | until 2000 | L (>=350MW) | E | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  | 2000-2005 | L (>=350MW) | Fa | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW 2013 (RWI 1997) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (Wagner 2004) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  | 2006-2010 | L (>=350MW) | Fb | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  | After 2010 | L (>=350MW) | H | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=100MW and <350MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=9MW and <100MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<9MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | VGB PowerTech 2011b*; OCGT | Ecofys 2014, DIW 2013 |  | DIW 2013 | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | van der Bergh and Delarue 2015 |  | DIW 2013 (Klobasa et al.. 2009) | ECOFYS 2014 (OCGT) |  | van der Bergh and Delarue 2015; DIW 2013 (Hundt et al. 2009) - OCGT | Hentschel 2016 (OCGT) |  | van der Bergh and Delarue 2015 (OCGT) | Brouwer 2015 (OCGT) |  | DIW (VGB Powertech 2011) | Brouwer 2010 (GT) |  | IEA 2016 (Gas Turbine) | Brouwer 2015 (GT) |  | DIW 2013 (IEA et al.. 2010) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 modern) | DIW 2013 (Meibom et al. 2008) |  | DIW 2013 (Kumar et al. 2012 median) | Kumar 2012 |  | Van der Bergh & Delarue 2015 | DIW 2013, Meibom et al. 2008 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | Parsons Brinckerhoff - DECC 2014 | DIW 2013, Meibom el al. 2000 |  | DIW 2013, Traber & Kemfert 2011
|  | Steam turbine |  | L (>=350MW) |  | DIW 2014 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | Kunz 2012 | van der Bergh & Delarue 2015 |  | van der Bergh & Delarue 2015 | IEA 2011a |  | Steck & Mauch 2006 | IEA 2011a |  | Steck & Mauch 2006 | van der Bergh and Delarue 2015 (gas fired steam plant)) |  | van der Bergh and Delarue 2015 (gas fired steam plant)) | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant |  | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (Capros 2011) | no data |  | no data | no data |  | no data | no data |  | no data | Kumar 2012 |  | Van der Bergh & Delarue 2015 | no data |  | no data | DIW 2013, Hundt el al. 2009 |  | DIW 2013, Hundt el al. 2009 | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=100MW and <350MW) |  | DIW 2014 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | Kunz 2012 | van der Bergh & Delarue 2015 |  | van der Bergh & Delarue 2015 | IEA 2011a |  | Steck & Mauch 2007 | IEA 2011a |  | Steck & Mauch 2007 | van der Bergh and Delarue 2015 (gas fired steam plant)) |  | van der Bergh and Delarue 2015 (gas fired steam plant)) | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant |  | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (Capros 2011) | no data |  | no data | no data |  | no data | no data |  | no data | Kumar 2012 |  | Van der Bergh & Delarue 2015 | no data |  | no data | DIW 2013, Hundt el al. 2009 |  | DIW 2013, Hundt el al. 2009 | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=9MW and <100MW) |  | DIW 2014 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | Kunz 2012 | van der Bergh & Delarue 2015 |  | van der Bergh & Delarue 2015 | IEA 2011a |  | Steck & Mauch 2008 | IEA 2011a |  | Steck & Mauch 2008 | van der Bergh and Delarue 2015 (gas fired steam plant)) |  | van der Bergh and Delarue 2015 (gas fired steam plant)) | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant |  | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (Capros 2011) | no data |  | no data | no data |  | no data | no data |  | no data | Kumar 2012 |  | Van der Bergh & Delarue 2015 | no data |  | no data | DIW 2013, Hundt el al. 2009 |  | DIW 2013, Hundt el al. 2009 | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<9MW) |  | DIW 2014 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | ECF 2010; OCGT |  | Kunz 2012 | van der Bergh & Delarue 2015 |  | van der Bergh & Delarue 2015 | IEA 2011a |  | Steck & Mauch 2009 | IEA 2011a |  | Steck & Mauch 2009 | van der Bergh and Delarue 2015 (gas fired steam plant)) |  | van der Bergh and Delarue 2015 (gas fired steam plant)) | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant |  | van der Bergh and Delarue 2015; DIW 2013 (Schuewer et al. 2010) - gas fired steam plant | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Capros 2011) |  | DIW 2013 (Capros 2011) | DIW 2013 (Traber & Kemfert 2011) |  | DIW 2013 (Capros 2011) | no data |  | no data | no data |  | no data | no data |  | no data | Kumar 2012 |  | Van der Bergh & Delarue 2015 | no data |  | no data | DIW 2013, Hundt el al. 2009 |  | DIW 2013, Hundt el al. 2009 | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  | Internal combustion |  | L (>=10MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | VGB PowerTech 2011b* | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  |  | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | M (>=5MW and <10MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | VGB PowerTech 2011b* | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  |  | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | S (>=2MW and <5MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | VGB PowerTech 2011b* | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  |  | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  |  |  | XS (<2MW) |  | own calculations |  | own calculations | - |  | - | - |  | - | - |  | - | Traber & Kemfert 2011 |  | VGB PowerTech 2011b* | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  |  | DIW 2013, Traber & Kemfert 2011 |  | DIW 2013, Traber & Kemfert 2011
|  | CCGT (CHP) |  |  |  | - |  | - | Brouwer 2015 |  | Fraunhofer IFAM 2014 | Fraunhofer IFAM 2014 |  | Study of Parliament Group 1992-2001 | Study of Parliament Group 1992-2001 |  | Industrial Efficiency Technology Database 2010 | ECF 2010 |  | Bertsch 2016 | DIW 2013 |  | DIW 2013 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (ECF 2010) |  | Bertsch 2016 | no data |  | no data | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Gas turbine (CHP) |  |  |  | - |  | - | no data |  | no data | Brouwer 2015 |  | Fraunhofer IFAM 2014 | Study of Parliament Group 1992-2001 |  | Fraunhofer IFAM 2014 | US EPA, 2014/15 Catalog of CHP Technologies |  | US EPA, 2014/15 Catalog of CHP Technologies | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | Hentschel 2016 |  | Hentschel 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | US EPA 2014/15 |  | US EPA 2014/15
|  | Internal combustion (CHP) |  |  |  | - |  | - | https://powergen.gepower.com/products/reciprocating-engines.html |  | https://powergen.gepower.com/products/reciprocating-engines.html | https://powergen.gepower.com/products/reciprocating-engines.html |  | https://powergen.gepower.com/products/reciprocating-engines.html | https://powergen.gepower.com/products/reciprocating-engines.html |  | https://powergen.gepower.com/products/reciprocating-engines.html | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | US EPA 2015 |  | US EPA 2015 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | US EPA 2014/15 |  | US EPA 2014/15
|  | Backpressure steam turbine (CHP) |  |  |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | US EPA 2014/15 |  | Fraunhofer IFAM 2014 | Study of Parliament Group 1992-2001 |  | Bureau of Energy Efficiency | US EPA, 2014/15 Catalog of CHP Technologies |  | US EPA, 2014/15 Catalog of CHP Technologies | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Extraction steam turbine (CHP) |  |  |  | - |  | - | Fraunhofer IFAM 2014 |  | Fraunhofer IFAM 2014 | US EPA 2014/15 |  | Fraunhofer IFAM 2014 | Bureau of Energy Efficiency |  | Fraunhofer IFAM 2014 | US EPA, 2014/15 Catalog of CHP Technologies |  | US EPA, 2014/15 Catalog of CHP Technologies | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Uranium | PWR (Pressurized water reactor) |  | L (>=750MW) |  | Bertsch 2016, Siemens 2010 |  | Siemens 2010 | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | Ecofys 2014 |  | Ecofys 2014, DIW 2013 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | DIW 2013 (ECF 2010) |  | DIW 2013 (Ehlers 2011) | DIW 2013 (ECF 2010) |  | DIW 2013 (Schuewer et al. 2010) | Brouwer 2015 |  | DIW 2013 (Severance 2009) | DIW 2013 (Risto & Kivisto 2008) |  | DIW 2013 (ECF 2010) | DIW 2013 (ECF 2010) |  | DIW 2013 (Risto & Kivisto 2008) | no data |  | no data | no data |  | no data | DIW 2-13 (dena 2005) |  | DIW 2013 (Ehlers 2011) | no data |  | no data | Black & Veatch 2012 |  | Brouwer 2015 | Siemens AG 2010 |  | Brouwer 2015 | Lund et al. 2015 |  | Grimm 2007
|  |  |  | M (<750MW) |  | Bertsch 2016, Siemens 2010 |  | Siemens 2010 | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | Ecofys 2014 |  | Ecofys 2014, DIW 2013 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | DIW 2013 (ECF 2010) |  | DIW 2013 (Ehlers 2011) | DIW 2013 (ECF 2010) |  | DIW 2013 (Schuewer et al. 2010) | Brouwer 2015 |  | DIW 2013 (Severance 2009) | DIW 2013 (Risto & Kivisto 2008) |  | DIW 2013 (ECF 2010) | DIW 2013 (ECF 2010) |  | DIW 2013 (Risto & Kivisto 2008) | no data |  | no data | no data |  | no data | DIW 2-13 (dena 2005) |  | DIW 2013 (Ehlers 2011) | no data |  | no data | Black & Veatch 2012 |  | Brouwer 2015 | Siemens AG 2010 |  | Brouwer 2015 | Lund et al. 2015 |  | Grimm 2007
|  | BWR (Boiling water reactor) |  | L (>=750MW) |  | Bertsch 2016, Siemens 2010 |  | Bertsch 2016 | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | Ecofys 2014 |  | Ecofys 2014, DIW 2013 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | DIW 2013 (ECF 2010) |  | DIW 2013 (Ehlers 2011) | DIW 2013 (ECF 2010) |  | DIW 2013 (Schuewer et al. 2010) | Brouwer 2015 |  | DIW 2013 (Severance 2009) | DIW 2013 (Risto & Kivisto 2008) |  | DIW 2013 (ECF 2010) | DIW 2013 (ECF 2010) |  | DIW 2013 (Risto & Kivisto 2008) | no data |  | no data | no data |  | no data | DIW 2-13 (dena 2005) |  | DIW 2013 (Ehlers 2011) | no data |  | no data | Black & Veatch 2012 |  | Brouwer 2015 | Siemens AG 2010 |  | Brouwer 2015 | Lund et al. 2015 |  | Grimm 2007
|  |  |  | M (<750MW) |  | Bertsch 2016, Siemens 2010 |  | Bertsch 2016 | - |  | - | - |  | - | - |  | - | DIW 2014 |  | dena 2008 | Ecofys 2014 |  | Ecofys 2014, DIW 2013 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | van der Bergh and Delarue 2015 |  | ECOFYS 2014 | DIW 2013 (ECF 2010) |  | DIW 2013 (Ehlers 2011) | DIW 2013 (ECF 2010) |  | DIW 2013 (Schuewer et al. 2010) | Brouwer 2015 |  | DIW 2013 (Severance 2009) | DIW 2013 (Risto & Kivisto 2008) |  | DIW 2013 (ECF 2010) | DIW 2013 (ECF 2010) |  | DIW 2013 (Risto & Kivisto 2008) | no data |  | no data | no data |  | no data | DIW 2-13 (dena 2005) |  | DIW 2013 (Ehlers 2011) | no data |  | no data | Black & Veatch 2012 |  | Brouwer 2015 | Siemens AG 2010 |  | Brouwer 2015 | Lund et al. 2015 |  | Grimm 2007
| Biomass | Steam turbine |  |  |  | Bertsch , 2016, EURELETRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | Bertsch 2016 | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (PIK 2011) |  | DIW 2013 (Peter & Lehmann 2008) | DIW 2013 (DLR & SRU 2010) |  | DIW 2013 (DLR & SRU 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Back-pressure steam turbine (CHP) |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | no data |  | no data | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (DLR & SRU 2010) |  | DIW 2013 (DLR & SRU 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Extraction steam turbine (CHP) |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | no data |  | no data | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (DLR & SRU 2010) |  | DIW 2013 (DLR & SRU 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Organic Rankine-cycle (CHP) |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | no data |  | no data | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Biogas | Internal combustion |  |  |  | - |  | - | - |  | - | - |  | - | - |  | - | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2010) |  | DIW 2013 (Nagi 2012) | no data |  | no data | DIW 2013 |  | DIW 2013 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Internal combustion (CHP) |  |  |  | - |  | - | Yingjan et al., 2014 |  | Yingjan et al., 2014 | Yingjan et al., 2014 |  | Yingjan et al., 2014 | Yingjan et al., 2014 |  | Yingjan et al., 2014 | Bertsch 2016 |  | Bertsch 2016 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (Nagi 2012) |  | DIW 2013 (IEA 2010) | DIW 2013 (IEA et al.. 2010) |  | DIW 2013 (DLR & SRU 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Water | Conventional hyrdoeletric turbine |  | L (>=30MW) | Run-of-river | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (VGB PowerTech 2011) |  | DIW 2013 (Wissel 2008) | IEA 2016 (Hydro, large) |  | IRENA 2015 (Large hydro >10MWe) | IEA 2016 (Hydro, large) |  | IRENA 2015 (Large hydro >10MWe) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | M (>=10MW and <30MW) |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (VGB PowerTech 2011) |  | DIW 2013 (Wissel 2008) | IRENA 2015 (Large hydro >10MWe) |  | IRENA 2015 (Large hydro >10MWe) | IRENA 2015 (Large hydro >10MWe) |  | IRENA 2015 (Large hydro >10MWe) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | S (>=1MW and <10MW) |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (VGB PowerTech 2011) |  | DIW 2013 (Wissel 2008) | IRENA 2015 (Small hydro 1-10MWe) |  | IEA 2016 (Hydro, small) | IRENA 2015 (Small hydro 1-10MWe) |  | IEA 2016 (Hydro, small) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | XS (<1MW) |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (VGB PowerTech 2011) |  | DIW 2013 (Wissel 2008) | IRENA 2015 (Very small hydro, up to 1 MWe) |  | IRENA 2015 (Very small hydro, up to 1 MWe) | IRENA 2015 (Very small hydro, up to 1 MWe) |  | IRENA 2015 (Very small hydro, up to 1 MWe) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | L (>=75MW) | Reservoirs | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2011) |  | DIW 2013 (IEA 2010) | IEA 2016 (Hydro, large) |  | IRENA 2015 (Large hydro >10MWe) | IEA 2016 (Hydro, large) |  | IRENA 2015 (Large hydro >10MWe) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | M (>=10MW and <75MW) |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2011) |  | DIW 2013 (IEA 2010) | IRENA 2015 (Large hydro >10MWe) |  | IRENA 2015 (Large hydro >10MWe) | IRENA 2015 (Large hydro >10MWe) |  | IRENA 2015 (Large hydro >10MWe) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | S (>=1MW and <10MW) |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2011) |  | DIW 2013 (IEA 2010) | IRENA 2015 (Small hydro 1-10MWe) |  | IEA 2016 (Hydro, small) | IRENA 2015 (Small hydro 1-10MWe) |  | IEA 2016 (Hydro, small) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | XS (<1MW) |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2011) |  | DIW 2013 (IEA 2010) | IRENA 2015 (Very small hydro, up to 1 MWe) |  | IRENA 2015 (Very small hydro, up to 1 MWe) | IRENA 2015 (Very small hydro, up to 1 MWe) |  | IRENA 2015 (Very small hydro, up to 1 MWe) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Pumped-storage |  | L (>=75MW) |  | IEA 2014 |  | IEA 2014 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (EWI 2012) |  | EIA 2013 | EIA 2013 |  | EIA 2013 | EIA 2013 |  | EIA 2013 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | M (>=10MW and <75MW) |  | IEA 2014 |  | IEA 2014 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (EWI 2012) |  | EIA 2013 | EIA 2013 |  | EIA 2013 | EIA 2013 |  | EIA 2013 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | S (>=1MW and <10MW) |  | IEA 2014 |  | IEA 2014 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (EWI 2012) |  | EIA 2013 | EIA 2013 |  | EIA 2013 | EIA 2013 |  | EIA 2013 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  |  |  | XS (<1MW) |  | IEA 2014 |  | IEA 2014 | - |  | - | - |  | - | - |  | - | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (EWI 2012) |  | EIA 2013 | EIA 2013 |  | EIA 2013 | EIA 2013 |  | EIA 2013 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Tidal |  |  |  | EURELECTRIC 2003 |  | EURELECTRIC 2003 | - |  | - | - |  | - | - |  | - | no data |  | no data | IRENA 2014-15 |  | IRENA 2014-15 | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2010) |  | DIW 2013 (IEA 2010) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
|  | Wave |  |  |  | - |  | - |  |  | - | - |  | - | - |  | - | Pelc, Fujita, 2002, Renewable energy from the ocean |  | Pelc, Fujita, 2002, Renewable energy from the ocean | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | DIW 2013 (IEA 2010) |  | DIW 2013 (Black & Veatch 2012) | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data | no data |  | no data
| Solar | Photovoltaic (RESIDENTIAL ROOFTOP) |  | XS (<0.01MW)
|  | Photovoltaic (COMMERCIAL ROOFTOP) |  | S (>=0.01MW and <0.5MW)
|  | Photovoltaic (UTILITY SCALE) |  | L (>=1MW and <100MW)
19 |  | Photovoltaic (VERY LARGE SCALE) |  | L (>=100MW)
| * (CHP) | cogeneration technologies
Note on AN3: all EUR/kWa; Nuclear (€/MWh)
Note on AO3: all EUR/kWa; Nuclear (€/MWh)
Note on AP3: all EUR/kWa; Nuclear (€/MWh)